{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":46,"n_cols":18,"rows_kept":46,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWD-DZXE"]
[]
[]
[]
[]
["","","","","","EWWD340DZXEA1","EWWD470DZXEA1","EWWD570DZXEA1","EWWD670DZXEA2","EWWD680DZXEA2","EWWD740DZXEA1","EWWD950DZXEA2","EWWDC10DZXEA3","EWWDC11DZXEA2","EWWDC14DZXEA3","EWWDC15DZXEA2","EWWDC17DZXEA3","EWWDC22DZXEA3"]
["Cooling capacity","Nom.","","","kW","341","474","566","670","682","742","946","1,038","1,130","1,437","1,478","1,685","2,173"]
["Capacity control","Method","","","","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable"]
["","Minimum capacity","","","%","29","20","20","15","15","17","10","10","10","7","9","7","6"]
["Power input","Cooling","","Nom.","kW","69.9","93.5","108","138.4","138","131","186","210","216","288","263","329","393"]
["EER","","","","","4.88","5.07","5.22","4.84","4.91","5.65","5.08","4.94","5.23","4.98","5.6","5.12","5.53"]
["ESEER","","","","","7.81","7.83","8.11","7.52","8","8.09","7.96","","8.26","","8.22"]
["Dimensions","Unit","","Depth","mm","3,625","3,625","3,625","3,625","3,585","3,585","3,585","4,688","3,580","4,793","3,580","4,768","4,812"]
["","","","Height","mm","1,865","1,865","1,865","1,985","1,985","1,985","1,985","2,082","2,200","2,083","2,200","2,225","2,290"]
["","","","Width","mm","1,055","1,055","1,055","1,160","1,160","1,160","1,160","1,510","1,270","1,510","1,270","1,510","1,510"]
["Weight","Unit","","","kg","1,750","1,950","2,050","2,850","2,850","2,650","3,000","4,400","3,700","4,700","3,900","5,100","5,900"]
["","Operation weight","","","kg","2,033","2,276","2,407","3,197","3,354","3,162","3,568","4,970","4,412","5,370","4,699","5,890","6,920"]
["Water heat exchanger - evaporator","Type","","","","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube"]
["","Water volume","","","l","70","96","107","107","134","134","156","207.3","199","317.4","229","317.4","444.3"]
["","Water flow rate","","Nom.","l/s","16.4","22.7","27.1","32","32.7","35.6","45.3","","54.1","","70.9"]
["Water heat exchanger - condenser","Type","","","","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Flooded Shell & Tube","Shell and tube","Flooded Shell & Tube","Shell and tube","Flooded Shell & Tube","Flooded Shell & Tube"]
["","Water flow rate","","Nom.","l/s","19.6","27","32.1","38.6","39.1","41.6","53.9","","64.1","","83"]
["Compressor","Type","","","","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor","Oil free centrifugal compressor"]
["","Quantity","","","","1","1","1","2","2","1","2","3","2","3","2","3","3"]
["Sound power level","Cooling","","Nom.","dBA","87.9","88.9","89.9","91.1","91","91.1","92","98","93.3","99","94.3","100","101"]
["Sound pressure level","Cooling","","Nom.","dBA","69.6","70.6","71.6","72.6","72.6","72.6","73.6","79","74.6","80","75.6","81","82"]
["Operation range","Evaporator","Cooling","Min.","°CDB","4","4","4","4","4","4","4","4","4","4","4","4","4"]
["","","","Max.","°CDB","20","20","20","20","20","20","20","20","20","20","20","20","20"]
["","Condenser","Cooling","Min.","°CDB","20","20","20","20","20","20","20","20","20","20","20","20","20"]
["","","","Max.","°CDB","55","55","42","55","55","42","55","55","42","55","42","42","42"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","Charge","","","kg","130","130","130","120","200","190","200","350","250","400","250","420","470"]
["","Circuits","","Quantity","","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","GWP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0"]
["","","","","","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(2) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced.","(3) - In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C"]
["","","","","","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1","(5) - Maximum current for wires sizing: compressor full load ampere x 1.1"]
["","","","","","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data.","(6) - All data are subject to change without notice. Please refer to the unit nameplate data."]
["","","","","","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(7) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744"]
["","","","","","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(8) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(9) - Maximum unit current for wires sizing is based on minimum allowed voltage."]