{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":43,"n_cols":10,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWH-VZPS"]
[]
[]
[]
[]
["","","","","EWWH370VZPSA1","EWWH530VZPSA1","EWWH680VZPSA1","EWWH880VZPSA2","EWWHC12VZPSA2","EWWHC13VZPSA2"]
["Cooling capacity","Nom.","","kW","369","525","677","884","1,180","1,295"]
["Capacity control","Method","","","Variable","Variable","Variable","Variable","Variable","Variable"]
["","Minimum capacity","","%","20","20","20","10","10","10"]
["Power input","Cooling","Nom.","kW","64.7","94.9","119","166","221","247"]
["EER","","","","5.71","5.53","5.67","5.34","5.35","5.25"]
["ESEER","","","","7.9","8.64","8.83","8.54","8.85","9"]
["Dimensions","Unit","Depth","mm","3,750","3,822","3,822","4,508","4,750","4,874"]
["","","Height","mm","2,108","2,430","2,487","2,302","2,500","2,493"]
["","","Width","mm","1,179","1,287","1,303","1,579","1,610","1,769"]
["Weight","Unit","","kg","3,247","4,082","4,346","6,310","7,530","8,250"]
["","Operation weight","","kg","3,375","4,349","4,660","6,900","8,300","9,200"]
["Water heat exchanger - evaporator","Type","","","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube"]
["","Water volume","","l","96","168","199","320","380","480"]
["Water heat exchanger - condenser","Type","","","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube"]
["Compressor","Type","","","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor"]
["","Quantity","","","1","1","1","2","2","2"]
["Sound power level","Cooling","Nom.","dBA","99","105","105","106","107","109"]
["Sound pressure level","Cooling","Nom.","dBA","80","86","86","87","88","89"]
["Refrigerant","Charge","","kg","100","150","180","290","320","350"]
["","Circuits","Quantity","","1","1","1","2","2","2"]
["","GWP","","","7","7","7","7","7","7"]
["Refrigerant circuit","Charge","","kg","100","150","180","290","320","350"]
["Power supply","Phase","","","3~","3~","3~","3~","3~","3~"]
["","Frequency","","Hz","50","50","50","50","50","50"]
["","Voltage","","V","400","400","400","400","400","400"]
["Notes","","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0"]
["","","","","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744"]
["","","","","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C"]
["","","","","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1"]
["","","","","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options."]
["","","","","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data."]
["","","","","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]
["","","","","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced."]