{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":63,"n_cols":9,"rows_kept":63,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYA-DW1P-H-"]
[]
[]
[]
[]
["","","","","","EWYA009DAW1P-H-","EWYA011DAW1P-H-","EWYA014DAW1P-H-","EWYA016DAW1P-H-"]
["Sound pressure level","Cooling","","Nom.","dBA","44.0","47.7","50.8","51.0"]
["Hydraulic components","Expansion vessel","","Volume","l","8","8","8","8"]
["Operation range","Air side","Cooling","Min.","°CDB","10","10","10","10"]
["","","","Max.","°CDB","43","43","43","43"]
["","","Heating","Max.","°CDB","25","25","25","25"]
["","","","Min.","°CDB","-25","-25","-25","-25"]
["","Water side","Heating","Min.","°CDB","9 (7)","9 (7)","9 (7)","9 (7)"]
["","","","Max.","°CDB","60 (7)","60 (7)","60 (7)","60 (7)"]
["","","Cooling","Max.","°CDB","22","22","22","22"]
["","","","Min.","°CDB","5","5","5","5"]
["Refrigerant charge","Per circuit","","","kg","3.80","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6","2.6"]
["Compressor","Type","","","","Hermetically sealed swing inverter compressor","Hermetically sealed swing inverter compressor","Hermetically sealed swing inverter compressor","Hermetically sealed swing inverter compressor"]
["","Starting method","","","","Inverter driven","Inverter driven","Inverter driven","Inverter driven"]
["","Quantity","","","","1","1","1","1"]
["Weight","Unit","","","kg","147","147","147","147"]
["Air heat exchanger","Type","","","","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler"]
["EER","","","","","3.35 (1), 5.34 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Refrigerant","GWP","","","","675.0","675.0","675.0","675.0"]
["","Type","","","","R-32","R-32","R-32","R-32"]
["","Circuits","","Quantity","","1","1","1","1"]
["","Control","","","","Electronic expansion valve","Electronic expansion valve","Electronic expansion valve","Electronic expansion valve"]
["Fan motor","Speed","Cooling","Nom.","rpm","500","550","650","650"]
["","","Heating","Nom.","rpm","400","450","550","650"]
["Cooling capacity","Nom.","","","kW","9.35 (1), 9.10 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Water heat exchanger","Water volume","","","l","2","2","2","2"]
["","Minimum water volume in the system","","","l","50 (6)","50 (6)","50 (6)","50 (6)"]
["","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["Power input","Cooling","","Nom.","kW","2.79 (1), 1.71 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["","Heating","","Nom.","kW","1.91 (3), 2.43 (4)","2.18 (3), 2.68 (4)","2.46 (3), 3.42 (4)","3.53 (3), 4.56 (4)"]
["Sound power level","Cooling","","Nom.","dBA","65.5","67.0","69.0","69.0"]
["COP","","","","","4.91 (3), 3.71 (4)","4.83 (3), 3.66 (4)","4.87 (3), 3.64 (4)","4.53 (3), 3.51 (4)"]
["Dimensions","Unit","","Width","mm","1,380","1,380","1,380","1,380"]
["","","","Depth","mm","460","460","460","460"]
["","","","Height","mm","870","870","870","870"]
["Capacity control","Method","","","","Variable (inverter)","Variable (inverter)","Variable (inverter)","Variable (inverter)"]
["Space heating","Average climate water outlet 35°C","General","ηs (Seasonal space heating efficiency)","%","190","186","185","185"]
["","","","Seasonal space heating eff. class","","A+++","A+++","A+++","A+++"]
["","","","SCOP","","4.82","4.73","4.70","4.69"]
["","Average climate water outlet 55°C","General","Seasonal space heating eff. class","","A++","A++","A++","A++"]
["","","","ηs (Seasonal space heating efficiency)","%","135","132","134","132"]
["","","","SCOP","","3.44","3.37","3.42","3.37"]
["Fan","Air flow rate","Heating","Nom.","m³/min","48.0","55.8","70.4","85.0"]
["","","Cooling","Nom.","m³/min","63","70","85","85"]
["Heating capacity","Nom.","","","kW","9.37 (3), 9.00 (4)","10.6 (3), 9.82 (4)","12.0 (3), 12.5 (4)","16.0 (3), 16.0 (4)"]
["Compressor","Starting method","","","","Inverter","Inverter","Inverter","Inverter"]
["Power supply","Phase","","","","3~","3~","3~","3~"]
["","Name","","","","W1","W1","W1","W1"]
["","Frequency","","","Hz","50","50","50","50"]
["","Voltage","","","V","400","400","400","400"]
["Notes","","","","","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB"]
["","","","","","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB"]
["","","","","","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825"]
["","","","","","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual."]
["","","","","","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing"]