{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":59,"n_cols":8,"rows_kept":59,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYT-B-SS"]
[]
[]
[]
[]
["","","","","","EWYT300B-SSA2-VFDFAN","EWYT490B-SSA2","EWYT490B-SSA2-VFDFAN"]
["Sound pressure level","Cooling","","Nom.","dBA","74.5","","76.6"]
["Compressor","Type","","","","Scroll compressor","","Scroll compressor"]
["","Starting method","","","","Direct on line","","Direct on line"]
["","Quantity","","","","4","","5"]
["Weight","Operation weight","","","kg","2,114","","3,207.27"]
["","Unit","","","kg","2,100","","3,180"]
["Air heat exchanger","Type","","","","High efficiency fin and tube type","","High efficiency fin and tube type"]
["EER","","","","","2.64","","2.53"]
["Refrigerant","Type","","","","R-32","","R-32"]
["","Circuits","","Quantity","","2","","2"]
["","Charge","","","kg","41.7","","60.3"]
["Fan motor","Drive","","","","VFD driven","","VFD driven"]
["Cooling capacity","Nom.","","","kW","270","","434"]
["IPLV","","","","","4.35","","4.68"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","88.9","","88.9"]
["Power input","Cooling","","Nom.","kW","102","","171"]
["Sound power level","Cooling","","Nom.","dBA","94","","96.6"]
["Dimensions","Unit","","Width","mm","2,282","","2,282"]
["","","","Depth","mm","3,225","","4,125"]
["","","","Height","mm","2,514","","2,514"]
["Capacity control","Minimum capacity","","","%","22","","22"]
["","Method","","","","Step","","Step"]
["Casing","Material","","","","Galvanized and painted steel sheet","","Galvanized and painted steel sheet"]
["","Colour","","","","Ivory white","","Ivory white"]
["Fan","Type","","","","Direct propeller","","Direct propeller"]
["","Quantity","","","","5","","8"]
["Power supply","Phase","","","","3~","","3~"]
["","Voltage range","","Max.","%","10","","10"]
["","","","Min.","%","-10","","-10"]
["","Frequency","","","Hz","50","","50"]
["","Voltage","","","V","400","","400"]
["Unit","Max unit current for wires sizing","","","A","255","","417"]
["","Starting current","","Max","A","564","","712"]
["","Running current","Cooling","Nom.","A","175","","292"]
["","","","Max","A","232","","379"]
["Notes","","","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018"]
["","","","","","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018"]
["","","","","","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N"]
["","","","","","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter"]
["","","","","","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i"]
["","","","","","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition"]
["","","","","","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request."]
["","","","","","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options."]
["","","","","","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only."]
["","","","","","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water"]
["","","","","","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current"]
["","","","","","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current."]
["","","","","","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book"]
["","","","","","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data."]