{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":95,"n_cols":23,"rows_kept":95,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RWEYQ-T9"]
[]
[]
[]
[]
["","","","","","RWEYQ8T9Y1B","RWEYQ10T9Y1B","RWEYQ12T9Y1B","RWEYQ14T9Y1B","RWEYQ16T9Y1B","RWEYQ18T9Y1B","RWEYQ20T9Y1B","RWEYQ24T9Y1B","RWEYQ26T9Y1B","RWEYQ28T9Y1B","RWEYQ22T9Y1B","RWEYQ30T9Y1B","RWEYQ32T9Y1B","RWEYQ34T9Y1B","RWEYQ36T9Y1B","RWEYQ38T9Y1B","RWEYQ40T9Y1B","RWEYQ42T9Y1B"]
["Sound pressure level","Cooling","","Nom.","dBA","48.0 (10)","50.0 (10)","56.0 (10)","58.0 (10)","51.0 (10)","52.0 (10)","53.0 (10)","59.0 (10)","60.0 (10)","61.0 (10)","57.0 (10)","55.0 (10)","58.0 (10)","60.0 (10)","61.0 (10)","62.0 (10)","62.0 (10)","63.0 (10)"]
["Standard Accessories","Installation manual","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","Operation manual","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","Connection pipes","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","Water supply piping with strainer","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["Capacity range","HP","","","","8","10","12","14","16","18","20","24","26","28","22","30","32","34","36","38","40","42"]
["ηs,c","%","","","","326.8","307.8","359.0","330.7","307.6","308.7","298.1","342.6","322.5","306.1","311.3","308.3","318.2","342.5","352.3","338.8","341.4","332.9"]
["Maximum number of connectable indoor units","","","","","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)","64 (7)"]
["Space cooling","B Condition (30°C - 27/19), cooling tower (inlet/outlet) 26/*","","EERd","%","6.9","6.3","7.0","6.3","6.5","6.5","6.3","7.0","6.6","6.3","6.6","6.3","6.5","6.7","7.0","6.7","6.5","6.3"]
["","","","Pdc","kW","16.5","20.6","24.7","29.5","33.0","37.1","41.3","49.4","54.2","58.9","45.3","61.9","66.0","70.0","74.1","78.8","83.6","88.4"]
["","A Condition (35°C - 27/19), cooling tower (inlet/outlet) 30/35","","Pdc","kW","22.4","28.0","33.5","40.0","44.8","50.4","56.0","67.0","73.5","80.0","61.5","84.0","89.5","95.0","100.5","107.0","113.5","120.0"]
["","","","EERd","%","5.6","4.6","5.4","4.2","5.1","5.0","4.6","5.4","4.9","4.5","5.0","4.6","4.9","5.1","5.4","5.0","4.7","4.5"]
["","D Condition (20°C - 27/19), cooling tower (inlet/outlet) 18/*","","Pdc","kW","7.9","7.9","8.2","8.4","9.4","10.6","11.8","14.1","15.5","16.8","13.0","17.7","18.8","20.0","21.2","22.5","24.5","25.3"]
["","","","EERd","%","11.9","12.3","14.9","15.6","11.0","10.1","9.9","11.5","10.8","10.2","9.4","11.6","11.2","13.5","13.1","12.8","15.4","15.4"]
["","C Condition (25°C - 27/19), cooling tower (inlet/outlet) 22/*","","EERd","%","10.1","9.1","10.5","9.4","9.0","9.5","9.1","10.5","9.9","9.4","9.8","9.1","9.6","10.1","10.5","10.1","9.7","9.4"]
["","","","Pdc","kW","10.6","13.3","15.9","18.9","21.2","23.9","26.5","31.7","34.8","37.9","29.1","39.8","42.4","45.0","47.6","50.7","53.8","56.8"]
["SCOP","","","","","13.3","11.8","11.1","10.1","11.7","12.5","11.9","11.1","10.4","9.9","11.4","11.9","11.6","11.4","11.2","10.7","10.3","10.0"]
["Compressor","Type","","","","Hermetically sealed scroll inverter compressor","Hermetically sealed scroll inverter compressor","Hermetically sealed scroll inverter compressor","Hermetically sealed scroll inverter compressor"]
["Weight","Unit","","","kg","195","195","197","197"]
["Refrigerant","Charge","","","TCO2Eq","16.5","16.5","20.0","20.0"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","7.9","7.9","9.6","9.6"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["System","Outdoor unit module 2","","","","","","","","RWEYQ8T","RWEYQ10T","RWEYQ10T","RWEYQ12T","RWEYQ14T","RWEYQ14T","RWEYQ12T","RWEYQ10T","RWEYQ10T","RWEYQ12T","RWEYQ12T","RWEYQ12T","RWEYQ14T","RWEYQ14T"]
["","Outdoor unit module 3","","","","","","","","","","","","","","","RWEYQ10T","RWEYQ12T","RWEYQ12T","RWEYQ12T","RWEYQ14T","RWEYQ14T","RWEYQ14T"]
["","Outdoor unit module 1","","","","","","","","RWEYQ8T","RWEYQ8T","RWEYQ10T","RWEYQ12T","RWEYQ12T","RWEYQ14T","RWEYQ10T","RWEYQ10T","RWEYQ10T","RWEYQ10T","RWEYQ12T","RWEYQ12T","RWEYQ12T","RWEYQ14T"]
["Indoor index connection","Min.","","","","100.0","125.0","150.0","175.0","200.0","225.0","250.0","300.0","325.0","350.0","275.0","375.0","400.0","425.0","450.0","475.0","500.0","525.0"]
["","Max.","","","","300.0","375.0","450.0","525.0","600.0","675.0","750.0","900.0","975.0","1,050.0","825.0","1,125.0","1,200.0","1,275.0","1,350.0","1,425.0","1,500.0","1,575.0"]
["Cooling capacity","Prated,c","","","kW","22.4 (1)","28.0 (1)","33.5 (1)","40.0 (1)","44.8 (1)","50.4 (1)","56.0 (1)","67.0 (1)","73.5 (1)","80.0 (1)","61.5 (1)","84.0 (1)","89.5 (1)","95.0 (1)","100.5 (1)","107.0 (1)","113.5 (1)","120.0 (1)"]
["Recommended combination","","","","","4 x FXMQ50P7VEB","4 x FXMQ63P7VEB","6 x FXMQ50P7VEB","1 x FXMQ50P7VEB + 5 x FXMQ63P7VEB","4 x FXMQ63P7VEB + 2 x FXMQ80P7VEB","4 x FXMQ50P7VEB + 4 x FXMQ63P7VEB","8 x FXMQ63P7VEB","12 x FXMQ50P7VEB","7 x FXMQ50P7VEB + 5 x FXMQ63P7VEB","2 x FXMQ50P7VEB + 10 x FXMQ63P7VEB","6 x FXMQ50P7VEB + 4 x FXMQ63P7VEB","12 x FXMQ63P7VEB","6 x FXMQ50P7VEB + 8 x FXMQ63P7VEB","12 x FXMQ50P7VEB + 4 x FXMQ63P7VEB","18 x FXMQ50P7VEB","13 x FXMQ50P7VEB + 5 x FXMQ63P7VEB","8 x FXMQ50P7VEB + 10 x FXMQ63P7VEB","3 x FXMQ50P7VEB + 15 x FXMQ63P7VEB"]
["Space heating (Average climate)","TOL","","COPd (declared COP)","","7.2","6.1","5.8","5.8","6.1","6.6","6.2","5.8","5.3","4.9","6.0","6.2","6.1","5.9","5.8","5.4","5.1","4.9"]
["","","","Pdh (declared heating cap)","kW","25.0","31.5","37.5","45.0","50.0","56.5","63.0","75.0","82.5","90.0","69.0","94.5","100.5","106.5","112.5","120.0","127.5","135.0"]
["","","","Tol (temperature operating limit)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","8.9","8.8","8.8","9.2","8.6","8.7","9.6","11.5","12.7","13.9","10.6","17.7","17.7","17.6","17.6","18.5","19.6","20.8"]
["","","","COPd (declared COP)","","19.1","20.1","19.3","23.8","17.8","17.7","18.3","16.7","15.8","16.0","17.0","19.4","19.4","19.3","19.3","18.8","18.9","18.4"]
["","B Condition (2°C)","","COPd (declared COP)","","13.0","11.4","10.7","9.5","11.4","12.1","11.4","10.7","10.0","9.5","11.0","11.4","11.1","10.9","10.7","10.2","9.8","9.5"]
["","","","Pdh (declared heating cap)","kW","13.5","17.0","20.2","24.3","26.9","30.4","33.9","40.4","44.4","48.5","37.2","50.9","54.1","57.3","60.6","64.6","68.6","72.7"]
["","C Condition (7°C)","","COPd (declared COP)","","19.1","16.8","15.5","14.3","16.3","17.8","16.8","15.5","14.8","14.3","16.1","16.8","16.3","15.9","15.5","15.0","14.6","14.3"]
["","","","Pdh (declared heating cap)","kW","8.9","10.9","13.0","15.8","17.5","19.8","21.8","26.0","28.6","31.2","23.9","32.7","34.8","36.9","38.9","41.5","44.1","46.7"]
["","A Condition (-7°C)","","COPd (declared COP)","","8.1","7.1","6.6","5.8","6.9","7.5","7.1","6.6","6.1","5.7","6.8","7.1","6.9","6.7","6.6","6.3","6.0","5.7"]
["","","","Pdh (declared heating cap)","kW","22.1","27.9","33.2","39.6","44.2","50.0","55.7","66.3","73.0","79.6","61.0","83.6","88.9","94.2","99.5","106.2","112.8","119.4"]
["","TBivalent","","Pdh (declared heating cap)","kW","25.0","31.5","37.5","45.0","50.0","56.5","63.0","75.0","82.5","90.0","69.0","94.5","100.5","106.5","112.5","120.0","127.5","135.0"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","COPd (declared COP)","","7.2","6.1","5.8","5.8","6.1","6.6","6.2","5.8","5.3","4.9","6.0","6.2","6.1","5.9","5.8","5.4","5.1","4.9"]
["Piping connections","HP/LP gas","","OD","mm","15.9 (12), 19.1 (13)","19.1 (12), 22.2 (13)","19.1 (12), 28.6 (13)","22.2 (12), 28.6 (13)","22.2 (12), 28.6 (13)","22.2 (12), 28.6 (13)","28.6 (12), 28.6 (13)","28.6 (12), 34.9 (13)","28.6 (12), 34.9 (13)","28.6 (12), 34.9 (13)","28.6 (12), 28.6 (13)","28.6 (12), 34.9 (13)","28.6 (12), 34.9 (13)","28.6 (12), 34.9 (13)","28.6 (12), 41.3 (13)","41.3 (13), 34.9 (12)","41.3 (13), 34.9 (12)","41.3 (13), 34.9 (12)"]
["","Liquid","","OD","mm","9.52","9.52","12.70","12.70","12.70","15.90","15.90","15.90","19.10","19.10","15.90","19.10","19.10","19.10","19.10","19.10","19.10","19.10"]
["","","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","Total piping length","System","Actual","m","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)","500 (14)"]
["","Gas","","OD","mm","19.1 (11)","22.2 (11)","28.6 (11)","28.6 (11)","28.6 (11)","28.6 (11)","28.6 (11)","34.9 (11)","34.9 (11)","34.9 (11)","28.6 (11)","34.9 (11)","34.9 (11)","34.9 (11)","41.3 (11)","41.3 (11)","41.3 (11)","41.3 (11)"]
["","","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["SEER","","","","","8.4","7.9","9.2","8.5","7.9","7.9","7.7","8.8","8.3","7.9","8.0","7.9","8.2","8.8","9.0","8.7","8.7","8.5"]
["Sound power level","Cooling","","Nom.","dBA","65.0 (9)","71.0 (9)","72.0 (9)","74.0 (9)","68.0 (9)","72.0 (9)","74.0 (9)","75.0 (9)","76.0 (9)","77.0 (9)","75.0 (9)","76.0 (9)","76.0 (9)","76.0 (9)","77.0 (9)","78.0 (9)","78.0 (9)","79.0 (9)"]
["Dimensions","Unit","","Width","mm","767","767","767","767"]
["","","","Depth","mm","560","560","560","560"]
["","","","Height","mm","980","980","980","980"]
["ηs,h","%","","","","524.3","465.9","436.0","397.1","459.2","491.1","466.8","434.5","406.9","387.9","447.9","467.2","456.1","447.0","438.5","419.4","404.4","391.2"]
["Heating capacity","Prated,h","","","kW","25.0","31.5","37.5","45.0","50.0","56.5","62.5","75.0","82.5","90.0","69.0","94.5","100.5","106.5","112.5","120.0","127.5","135.0"]
["Power supply","Phase","","","","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~"]
["","Name","","","","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m."]
["","","","","","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(2) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998"]
["","","","","","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998","(3) - Cooling T3: Indoor temp 29°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,5m Level difference piping 0m Power input indoors included According to teststandard ISO 13256: 1998"]
["","","","","","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(4) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 7,6m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010"]
["","","","","","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010","(5) - Cooling T1: Indoor temp 27°CDB/19°CWB Water inlet temp 30°C Nom. waterflow Equivalent piping length 15,5m Level difference piping 0m Power input indoors included According to teststandard AHRI 1230: 2010"]
["","","","","","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(6) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(7) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)"]
["","","","","","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2.","(8) - Water flow rate for performance testing according to standard rating conditions of EN 14511-2."]
["","","","","","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates.","(9) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(10) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used","(11) - In case of heat pump system, gas pipe is not used"]
["","","","","","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system","(12) - In case of heat recovery system"]
["","","","","","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system","(13) - In case of heat pump system"]
["","","","","","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual","(14) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(15) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C"]
["","","","","","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(16) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(17) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(18) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(19) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set.","(20) - TOCA means the total value of each OC set."]
["","","","","","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%.","(21) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(22) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room.","(23) - Sound values are measured in a semi-anechoic room."]
["","","","","","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(24) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA"]
["","","","","","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(25) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power","(26) - Ssc: Short-circuit power"]
["","","","","","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual","(27) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination","(28) - Multi combination (10~54HP) data is corresponding with the standard multi combination"]